RAC DEVELOPMENT

Site Security & Starlink — Pole Installation Guide

Rodriguez Residence — Kanarraville, UT

# OVERVIEW

5 poles total. 4 camera poles at property corners (N/S/E/W). Starlink dish and its Renogy solar power system share the NORTH pole. No wire runs between poles. Everything is self-powered.

Pole layout: pull each pole 10 ft in from property edge so cameras aim inward across the site.

# MATERIALS

## All 5 poles:

- 4" schedule 40 steel pipe, 12 ft length

- 80 lb concrete — 2 bags per pole (10 bags total)

- Post hole: 18" diameter x 36" deep

## North pole only — Starlink + solar:

- LINOVISION pole mount bracket (already purchased)

- Renogy 100W monocrystalline panel (already purchased)

- Renogy 30A PWM charge controller (included in Renogy kit)

- 12V AGM or LiFePO4 battery — 50Ah minimum (purchase separately)

- Starlink Standard Kit (already purchased)

- Weatherproof NEMA 4X enclosure box, 12"x10"x6" minimum

- 10 AWG USE-2 solar wire, red/black, 15 ft

- 12V pure sine wave inverter, 150W minimum

- MC4 connectors and 30A inline fuse

- Cable clips/clamps for pole, qty 20

## Camera poles (x4):

- aosu solar wireless camera (1 per pole — 4 total, already purchased)

- Pole side-arm mount bracket, J-style (1 per camera pole)

# PART 1 — DIG AND SET ALL 5 POLES

⚠  Set all 5 poles in one session. Concrete needs 24 hrs cure before mounting any hardware.

- Mark pole locations

South pole: center of south property line facing road. North pole: center of north property line. East and West poles: centers of those lines. Pull each pole 10 ft inside the property boundary.

- Dig post holes

18" diameter, 36" deep. Use a towable auger — 5 holes in flat ground, about 1 hour total.

- Set poles in concrete

Drop pole in hole. Level plumb on two perpendicular sides. Pour 2 bags 80 lb concrete per hole. Work out air bubbles with a rod. Brace poles plumb. Leave 24 hours minimum before proceeding.

# PART 2 — MOUNT CAMERAS (4 POLES)

★  Do this after concrete is cured. Do not power cameras until Starlink WiFi is live.

- Mount side-arm bracket to each camera pole

Mount J-arm at 10-11 ft height. Camera face should point inward across property.

- Orient cameras

South pole camera aims north. North pole camera aims south. East aims west. West aims east. Full overlapping coverage of the entire site.

- Do not power cameras yet

aosu cameras require WiFi during setup. Leave unpowered until Part 3 is complete and Starlink is live.

# PART 3 — NORTH POLE: STARLINK + SOLAR POWER

★  Budget 3-4 hours for this pole. Most involved step in the whole install.

## Solar panel and charge controller:

- Mount LINOVISION bracket to pole

Set tilt angle 30-35 degrees. Panel faces south.

- Mount Renogy 100W panel to bracket

Secure panel. Route MC4 output cable down the pole with cable clips every 2 ft.

- Mount weatherproof enclosure to pole

Mount at 5-6 ft height — easy access for maintenance. Charge controller, battery, and inverter all live inside this box.

- Install battery in enclosure

12V AGM or LiFePO4, 50Ah minimum. Do not connect to anything yet.

- Wire charge controller — BATTERY FIRST

Connect battery terminals to charge controller battery input first. Then connect MC4 solar cable to controller PV input. Never connect PV before battery — damages controller.

- Install inverter in enclosure

Wire inverter DC input to battery: positive through 30A fuse then to inverter positive, negative direct. Do not power on yet.

## Starlink dish:

- Mount Starlink dish at pole top

Use included Starlink mounting pipe attached to pole top, or a side arm that gets the dish above the camera. Dish needs clear sky view — on flat open land any orientation works.

- Route Starlink cable down pole

Run cable down pole with clips. Connect cable to Starlink power brick. Power brick plugs into inverter AC outlet.

- Power up sequence

(1) Confirm battery charged — controller shows green. (2) Turn on inverter. (3) Plug in Starlink power brick to inverter outlet. Dish will self-orient — takes 5-15 minutes first boot.

- Activate Starlink and confirm internet

Download Starlink app. Connect phone to STARLINK WiFi. Complete activation. Run speed test — confirm internet is live before touching cameras.

# PART 4 — CONNECT CAMERAS

- Download aosu app

iOS or Android. Create account.

- Add each camera

Power each camera. In app: Add Device, scan QR code on camera body, connect to Starlink WiFi (use 2.4GHz band). Repeat for all 4.

- Confirm live video on all 4

Verify each camera shows live feed before adjusting aim.

- Final aim adjustment

Loosen bracket, adjust while watching live feed in app, retighten. Each camera should cover its half of the property with overlap at center.

- Enable motion alerts

Set motion detection zones in aosu app. Walk through each camera view to test.

# COMPLETION CHECKLIST

| Task | Done |
| --- | --- |
| All 5 poles set and plumb | [] |
| Concrete cured 24 hrs before loading any hardware | [] |
| Solar panel mounted south-facing, 30-35 degree tilt | [] |
| Charge controller wired — battery terminals first, then PV input | [] |
| Battery installed, charge controller shows voltage | [] |
| Inverter installed and wired to battery | [] |
| Starlink dish mounted at pole top | [] |
| Starlink powered up and self-oriented | [] |
| Starlink internet confirmed live — speed test passed | [] |
| All 4 cameras added to aosu app | [] |
| All 4 cameras showing live video feed | [] |
| Motion detection zones set and tested | [] |
| All cables secured to poles with clips | [] |

Questions: Craig Engel | RAC Development | (435) 229-7360 | racinc19@gmail.com