# Drawing Review — Single Panel Solar Fence

Review of drawings (705 panel, site plan, structural, EGING). Items to correct or clarify.

## 1. Orientation

Issue: Site plan shows Solar Fence at an angle; no North arrow. Action: State explicitly in RFP that fence must be East–West.

## 2. Post-to-footing

Drawings show posts sunk only. RFP offers both: Option A Sink posts, Option B Base plate (Owner provides detail).

## 3. L-angle

Use 0.75" × 2.5" L-angle, M8 at panel mounting holes (5–Φ11), welded to fence post.

## 4. Panel frame vs L-angle

Simple L-angle is for connecting panel to post via mounting holes, not the panel frame profile.

## 5. Material and finish

No powder coat; allow rust. Contractor specifies structural steel.

## 6. Structural dimensions

2×2 tube posts, 2×1 top, 1×2 bottom, 8'-0" panel height, 18"×36" footing, 3'-0" depth.

## 7. Solar conduit

Clarify in RFP whether conduit run to fence is in scope or owner/other trade.

Summary: Orientation E–W explicit; both post options; L-angle + M8 at holes; no powder coat; define conduit scope.